## Slide 1: Oilon ChillHeat heat pumps District heating and Cooling solutions
Jussi Alpua - Oilon / Žiga Debevec – Valmor

## Slide 2
Oilon in brief
Founded in 1961
Strong R&D focus
Family-owned company
Burners
Heat pumps
Turnover: EUR 85 million (2022)
Over 400 employees
One degree better

## Slide 3
Oilon dealers in over 60 countries
Oilon
Oilon dealer
One degree better

## Slide 4
Kokkola, Finland
Lahti, Finland
Lapua, Finland
Thomasville, USA
Wuxi, China
One degree better
One degree better

## Slide 5
Heat pumps and chillers
Founded in 2002
Over 300 large-scale projects
Install base ~200 MW
Oilon Partner for SEE Region (SI / CRO / SRB / BIH / MKD) since 2022
Main applications: high-temp. water production, process cooling and heating
10 employees
Solution partner for large Heat Pumps implementation
A 2022: Over 10MW of completed projects with HP

## Slide 6: Heating of the thermal park with a water-to-water heat pump: reduction of gas consumption for 95%
The waste thermal water used as a heat source for a 600 kW water-to-water heat pump for producing hot water at a temperature of 65°C
Trane RTWF 320 HSE, equipped with two screw compressors and a frequency inverter, enables high efficiency at partial loads (up to 10%)
Environmentally friendly refrigerant R1234ze
15y maintenance contract for Valmor

## Slide 7: Process Heating & Cooling: The production of cannabis for THC cultivation in North Macedonia
Total cooling capacity of 5.3MW & heating capacity of 3.4MW.
2x water-cooled chillers, each with a capacity of 1.1MW, for the production of chilled water at 5/10°C
The condenser water at 25/30°C serves as a heat source for two water-to-water heat pumps, each with a heating capacity of 1.68MW, for producing heat at temperature levels of 70/60°C
https://www.nytimes.com/2020/03/25/business/north-macedonia-marijuana.html

## Slide 8: Oilon Chillheat applications in district heating and cooling solutions
Combined heating and cooling (CHC)
CHC + Network booster
CHC + Network booster + Two-way district heating
Air to water heat pump
Hybrid solution for large real estates
Network booster
Heat recovery from wastewater
4th generation district heating
5th generation district heating
Geotherm – semi depth wells
Notes: Bullet 3 – not yet implemented; last bullet -> drilling has failed (up to 2km); hybrid solutions -> two way DH; wastewater -> municipal

## Slide 9: Combined heating and cooling (CHC)
More than 50 installations in Finland
5 on going installations
Recover cooling network waste heat
-> less carbon footprint
Distribute the heat according to the demand
 -> benefit of district heating network
Individually set cooling temperature
 -> independent of district cooling network
Wide capacity adjustment range
Compact size
Low GWP refrigerants
Notes: 58 projects, installed projects; 5 projects at the implementation stage; new business: sell cooling to the customers, collect energy to the DH network; buffer tank is the border; HP is getting the startup signal from the Tank temp. Measurement (bottom), HP is controling the water pump, after the tank is energy meter; after that is the customer’s pump. HP not connected to the BMS of the building; no connection of the third party system.
DH side: 40/50 deg (energy from subcooling) -> puting in supply line 70/95 deg; when temp. Level are below of 120 °C deg the capex in reasanobale. If over 120 the investment costs are unresanoble. Two-way valve for the minimum loads and to get enoguh pressure head from return to supply line; we monitor outlet temp. Level of HP and with this info we control pump + two-way valve.

## Slide 10: Combined heating and cooling (CHC) – Helen Oy
Heat source: Building cooling 15/10 ºC
Heat sink: District heating network 40/80 ºC
Cooling: 1900 kW
Heating capacity: 2850 kW
COPtot: 5,0
5 pcs Oilon ChillHeat heat pumps
Notes: System COP around 5; 2 pcs 450 + VFDs on 4 compressors

## Slide 11: Combined heating and cooling (CHC) – Valtatie 30
Heat source: Data Center 23/15 ºC
Heat sink: District heating network 50/95 ºC
Cooling: 2724 kW
Heating capacity: 4266 kW
COPtot: 4,42
6 pcs Oilon ChillHeat heat pumps

## Slide 12: CHC + Network booster
Cooling only in summer time, in winter time the HP would be shut-off
Additional PHE: cooling down the return line of DH
Heating up supply line -> producing the heat in DH with electricity
External machine room automation needed, - controls of HP are not self-sufficient for this solution
Notes: Cooling only in the summer time, rest of the time the HP would be shut off; LS -> PHE; if there is enough volume take out of the volume; take out temp. Of the return line (good for the powerplant); producing DH with the electricity; YOU NEED EXTERNAL MACHINE ROOM AUTOMATION

## Slide 13: CHC + Network booster – Lempäälän Lämpö Oy
Heat source:
  Building cooling (summer)
  Return flow of district heating (winter)
Cooling/heat recovery power: 600/986 kW
Heating capacity (summer/winter): 925/1390 kW
Heat sink: District heating network
Temperatures
  Heat source: 9 ºC / 30 ºC
  District heating: variable (max. 80 ºC)
2 pcs Oilon ChillHeat heat pumps

## Slide 14: CHC + Network booster + Two-way district heating
Heat is first used in the building, in case of left-over it can be run into district heating
Design idea, not yet installed
Notes: Not yet supplied; Heat is used first in the building, if there is left, we can run it to the district heating

## Slide 15
AWHP for high temperatures

## Slide 16
AWHP for high temperatures
Heat source:
  Air, min -15 C (1. stage AWHP, not in Oilon’s scope)
  Cooling network 14/6 C
Heat sink: District heating 77-98 ºC
Heating capacity: 9 100-10 320 kW
12 pcs Oilon ChillHeat heat pumps in 2. stage
Fortum Power and Heat Vermo II, Espoo Finland

## Slide 17: Hybrid solution for large real estate – Helen Oy
Heat source: Geotherm, Condensate from retail refrigeration, Wastewater, Cooling
Heat sink: Building heating, Domestic hot water, District heating
Cooling: 100 kW
Heating capacity: 115 kW
COP:
  Geotherm to building heating 2,94
  Cooling and district heating network 4,67
1 pcs Oilon ChillHeat heat pump
Finner of EHPA DecarBuilding series
Notes: 300m underground boreholes

## Slide 18: Network booster – Turku Energia Oy
Heat source: Return flow of district heating network 40 ºC
Heat sink: Supply flow of district heating network 70 ºC
Cooling: 160 kW
Heating capacity: 200kW
COPh: 4,70
1 pcs Oilon ChillHeat heat pump
Notes: Container solutions – not instaleld inside the facilities; advantage no need to run the powerplant to that high temperatures in spring, summer and autumn

## Slide 19: Heat booster – Napapiirin Energia ja Vesi Oy
Heat source: Return flow of district heating network 48-37 ºC
Heat sink: Supply flow of district heating network 70-85 ºC
Cooling: 170 kW
Heating capacity: 240kW
COPh: 3,44
1 pcs Oilon ChillHeat heat pump
Notes: Energy company can run the network lower (decreased the temp. level) – otherwise they would need to run the whole DH netowork higher just for one client

## Slide 20: Heat recovery wastewater – Etelä-Savon Energia Oy
Heat Source: Wastewater 9,5/4 ºC
Heat Sink: Local heating network 40/70 ºC
Cooling Capacity: 880 kW
Heating Capacity: 1300 kW
COPtot: 3,04
2 pcs Oilon ChillHeat heat pumps

## Slide 21: 4th generation district heating – Oulun Energia Oy
Heat source:
  Cooling network (summer) 14/7 ºC
  Return flow of district heating network (winter) 38/20 ºC
Heat sink:
  Local heating network and district heating network (Summer) 57/77 ºC
  Local heating network (Winter) 30/72 ºC
Cooling: 255 kW (Summer)
Heating capacity: 870 kW (Winter)
COP:
  Summer (tot) 3,84
  Winter: 3,93
1 pcs Oilon ChillHeat heat pump
Readiness for expansion (1 heat pump)
Notes: Old network + new network and between the HP; the old network as a heat source; the temp. Level is lower than in the old fashioned DH

## Slide 22: 5th generation district heating
Heat source: Low temperature network (30-40 ºC)
Heating capacity: 80 - 130 kW
Heat sink: Buildings
Temperatures
  Heating: 55 ºC
  Cooling and heating: 8 ºC / 55 ºC
4 pcs Oilon ChillHeat heat pumps
Notes: HP installed inside the buildings, utilizing low temp network as a heat source; if the building needs cooling, otherwise the condense is putting back in the main creed, e-on ecto creed

## Slide 23: Geotherm – Semi depth wells
Notes: Waiting for the first project to complete the installation -> the drilling is the problem

## Slide 24: Thank you!
www.oilon.com www.valmor.si
ziga.debevec@valmor.si / jussi.aplua@oilon.com